## Slide 1: Integrated Automation Safety Workshop
Shun Gao| 10/24/2019

## Slide 2: SIMATIC S7-1200 with Safety Integrated … right controller for basic control automation
    Basic control applications with safety requirements
    Stand-alone or networked machines
    Production engineering
    Special machines
Drilling
Cutting
Production
Packaging/ Labeling
Mounting
Grinding
Transportation

## Slide 3: SIMATIC S7-1200 with Safety Integrated …unique, innovative and efficient safety solution
  Minimization of types and parts
  Standard and fail-safe automation with just one controller
  PROFINET integrated
  Investment protection
  Simply add fail-safe modules to the Safety PLC
  Simple porting of existing application programs between S7-1200 <> S7-1500
  Certified according to EN 61508 2nd Edition and EN ISO 13849-1 PL e
  Field-proven Coded Processing instead of multi-processor system
  Maximum protection against manipulation
  Additional password for access to F configuration and F program
  Integrated Diagnostics
  Easy and rapid localization of faults through granular fault messages in plain text … also world wide via WEB-Server
+
+
+
+
+
Notes: 3

## Slide 4: SIMATIC S7-1200 with Safety Integrated …extreme flexibility for small machine manufactures
  Use as a standard controller with larger memory
+
  Use as a standard and safe controller
+
  Use as a safety controller
+
  S7-1212F S7-1214F S7-1215F
Notes: 4

## Slide 5: Simple or complex safety applications
SIMATIC S7-1200
KTPx00F Mobile
SINAMICS
Drive Safety functions
1
2
SIMATIC S7-1200
SINAMICS
F-Mobile Panel
2
3
SIMATIC S7-1500
Failsafe CPU/CPU Communication
3
4
Failsafe I-Device
4
1
1

## Slide 6: Benefits of the S7-1200F solution
Applications are always based on Standard plus Safety Automation
S7-1200 with Safety Integrated
+
> 2-3 safety functions
S7-200
Non-Siemens
Mitsubishi
Rockwell
Omron
Schneider
S7-1200
Safety Relays
Micro Safety PLC
Notes: 6

## Slide 7: Benefits of the S7-1200F solution
  Lower cost per F-IO point
  Less complex
    Only one software to program Standard and Safe program (eg Only one program to learn)
    Knowledge can be reused for 1500F
    Common library objects (preconfigured hardware or programs) may be created and reused
  Integrated diagnostics available for Standard and Safe via LED, Webserver, HMI and TIA Portal
  Easy access to F-IO status for HMI display
  Safety IO status can be used in the standard program
  Better scalability and more flexible design (eg distributed safety IO, Safe Motion, etc)
  Common manuals and less part numbers
**Based on FY18 List Prices

## Slide 8: Workshop Goals
Introduction of S7-1200F Wiring Demo.
Review Safety Functions of the Wiring Demo Unit.
Wiring diagrams and wiring exercise.
Commissioning and testing
Documentation and Safety Acceptance Test
Final notes

## Slide 9: Example 1: Simple Pump Control with Safety
Safety Requirement
  Pump control that meets ISO13849 Cat 4/PLe.
Safety Function
  When Estop is pressed, stop pump by disabling contactors
Standard Function
  Pump control using push buttons and indicators

## Slide 10: Simple Pump Control with Safety: Safety Relay vs. Safety PLC

## Slide 11: Simple Pump Control with Safety : Wiring Diagram for Safety Relay

## Slide 12: Simple Pump Control with Safety: Wiring Diagram for Safety PLC

## Slide 13: Example 2: Simple Pump and VFD Control with Safety
Safety Requirement
  Pump control that meets ISO13849 PLe.
  VFD STO that meets ISO13849 PLd.
Safety Function
  When Estop is pressed, stop pump by disabling contactors, stop VFD by turning off STO outputs
  When Door is open, stop VFD by turning off STO outputs.
Standard Function
  Pump control using push buttons and indicators
  VFD control using push buttons and indicators

## Slide 14: Simple Pump and VFD Control with Safety: Safety Relay vs. Safety PLC

## Slide 15: Simple Pump and VFD Control with Safety : Wiring Diagram for Safety Relays

## Slide 16: Simple Pump and VFD Control with Safety: Wiring Diagram for Safety PLC

## Slide 17: Workshop: Introduction of Wiring Demo Units
Start PB
RFIDDoorSwitch
GreenLEDWheel
EStop
Reset PB
Stop PB
RedPilotLight
GreenPilotLight
FailsafeCPU
FailsafeInput
FailsafeOutput

## Slide 18: Workshop: Goals
Wiring Exercise
  Simple Pump and VFD Control with Safety(Page 4 of the wiring diagram)
Commissioning and Testing
  Function test of S7-1200F demo unit using pre-loaded programs.
  Wiring Workshop Exercise

## Slide 19: Workshop: Wiring of Safety Input Module (Estop) -Technical Info
1
1
1
Local Estop: SIL 3, PL e, CAT 4 safety input wiring, 2 Normally Closed contacts on the Estop wired to 2 channels on the fail-safe Input Module, using Internal Sensor Supply. This redundant wiring checks for single point, cross wiring/short circuits related failures. (Test pulses from Internal Sensor Supply are sent through the contacts at regular intervals)
Note: Refer to S7-1200F User Manual (A5E03470344-AB) for wiring guidelines and configuration settings.
Note: Refer to “Safety Applications with the S7-1200 FC CPU” for application examples. (https://support.industry.siemens.com/cs/ww/en/view/109478932)
1
1
Notes: 19

## Slide 20: Workshop: Wiring of Safety Output Module (Contactors) -Technical Info
1. Contactor outputs: SIL 3, PL e, CAT 4, two contactors with positively guided contacts. This is then wired to 2 channels on the fail-safe Output Module.
2. Feedback: standard(non-safe) input, Normally Closed contacts(K1-31/32NC, K2-31/32NC) on each contactor wired in series, as the feedback signal.
This wiring of 2 contactors along with their feedback checks for single point, contact, cross wiring/short circuits related failures (Test pulses are sent through the contacts at regular intervals)
1
1
1
1
2
Notes: 20

## Slide 21: Workshop: Wiring of Safety Input Module (RFID Guard Switch) -Technical Info
Guard: SIL 3, PL e, safety input wiring, 2 Normally Open contacts on the Guard switch wired to 2 channels on the fail-safe Input Module, using External Sensor Supply required by the RFID switch.
Note: Refer to S7-1200F User Manual (A5E03470344-AB) for wiring guidelines and configuration settings.
Note: Refer to Support ID# 109478932 “Safety Applications with the S7-1200 FC CPU” for application examples. (https://support.industry.siemens.com/cs/ww/en/view/109478932)
Wiring example: actual channel number may be different!
1
1
1
1
1
Notes: 21

## Slide 22: Workshop: RFID Guard Switch -Technical Info
Function |  | PIN | Color
A1 | Ue | 1 | WHITE
X1 | Safety input 1 | 2 | BROWN
A2 | Ground (GND) | 3 | GREEN
OSSD1 | Safety output 1 | 4 | YELLOW
OUT | Diagnostics output | 5 | GREY
X2 | Safety input 2 | 6 | PINK
OSSD2 | Safety output 2 | 7 | BLUE
IN | No function | 8 | RED
Notes: 22