## Slide 1: Integrated Automation Safety Workshop
Shun Gao| 10/24/2019

## Slide 2: Hands-on Workshop: Introduction of Wiring Demo Units – Safety PLC Module
Start PB
RFIDDoorSwitch
GreenLEDWheel
EStop
Reset PB
Stop PB
RedPilotLight
GreenPilotLight
FailsafeCPU
FailsafeInput
FailsafeOutput

## Slide 3: Wiring Diagram – Pump Control using S7-1200F
Implement Pump Control safety function, using wiring diagram on page 2(Red wiring).
Proceed to next page for hands-on programming after wiring is done and demo unit has gone through power-up test(smoke test).
Notes: 3

## Slide 4
1
2
3
4
Create a new project
Name the project “Safety Wiring Demo”
Store the project in the \Student\Trainee folder on the desktop.
Press “Create”
Notes: 4

## Slide 5
1
Configure a device
Notes: 5

## Slide 6
1
2
3
4
5
6
7
Add a new device
Leave Device Name as default “PLC_1”
Select “Controllers”
Highlight CPU1212FC DC/DC/DC, “6ES7212-1AF40-0XB0”
Verify Part Number and Firmware=V4.2
Select “Open Device View”
Click “Add”
Notes: 6

## Slide 7
Highlight the CPU in the workspace
Using the Inspector Window, Select “Properties”, “General”
Highlight the “Startup” property
Change the properties as shown
  Warm restart – Run
  Startup CPU even if mismatch
1
2
2
3
4
Notes: 7

## Slide 8
Scroll down and highlight “System and clock memory”
Enable “System memory bits” & “Clock memory bits”
Note: System and Clock memory can be used for non-safe programs only.
1
2
2
Notes: 8

## Slide 9
Select the “Libraries” tab from the Task Card
Expand “Global libraries”—”Wiring Demo Workshop 2019”—”Master copies”—”1212F Fail-Safe”
Drag tags under “I/OTags” to the “PLC tags” folder of PLC_1; Drag “SafetyData” to the “Program blocks” folder of PLC_1
Note: We are using a library to save time typing in the Tags that will be used in this lab.
Note: Each Tag will be verified in the following steps
1
2
3
Notes: 9

## Slide 10
Stay on the “Device view” PLC_1
Select “Hardware catalog” from the Task Card
Drag F-DI (6ES7226-6BA32-0XB0) into Slot 2 of the PLC.
Drag F-DQ (6ES7226-6DA32-0XB0) into Slot 3 of the PLC.
1
3
4
2
Notes: 10

## Slide 11
Highlight the F-DI in Slot 2(double-click)
Select “Properties”
Under “Properties”, select “General”
Select “DI parameters”
Enable the “Short-circuit test”
1
2
3
5
4
Notes: 11

## Slide 12
Under “DI Parameters”, select “Channel parameters”, “Channel 0,8”
Make the following Changes
  Sensor evaluation – 1oo2 evaluation
  Discrepancy time – 250ms
  Sensor supply - Internal
1
2
Notes: 12

## Slide 13
Using the Inspector Window, Select “IO Tags”
Verify the following tag for Estop input only:
  I8.0 – Estop Input
1
2
Notes: 13

## Slide 14
Highlight the F-DQ in Slot 3(double-click)
Using the Inspector Window, Select “IO Tags”
Verify the following tags
  Pump Run Output K1
  Pump Run Output K2
  VS_ Pump Run Output K1(ValueStatus)
  VS_ Pump Run Output K2(ValueStatus)
Note: The ValueStatus inputs provide information on the validity of the corresponding channel value.
1
2
3
Notes: 14

## Slide 15
1
Right-click on “Main_Safety_RTG [FB1] program block
Select “Properties…”
Change the programming language to “LAD”
Press “OK”
Note: The default programming language is FBD, we will be working with LAD
2
3
4
Notes: 15

## Slide 16
1
Double click “Main_Safety_RTG1 [FB1]” for editing
Drag the NO contact, N_TRIG, and output coil from the instruction list to Network 1
Add boolean tags “SafetyReset” and “SafetyResetOneshot” to the Static area of the tag table.
Drag and drop tags from static tag table to the ladder logic.
Select “Default tag table” by single-click. Drag and drop tag(s) from “Details view” to the ladder logic.
2
3
4
5
5
Notes: 16

## Slide 17
2
Go to Network 2
Drag the “ACK_GL” block from the “Safety functions” folder of “Basic instructions” to Network 1
When the window appears, select “Multi-Instance”
Leave Instance Data name as default
Press “OK”
3
4
5
1
Notes: 17

## Slide 18
3
1
Drag and drop tag “SafeReset” from static tag table to the ladder logic.
Notes: 18

## Slide 19
Drag “ESTOP1” from the Safety Functions Folder and place it on Network 3 as shown.
Fill in tags as shown.
Note: Be sure to use the Multi-Instance option for the Instance Data when prompted during insertion the ESTOP1 block. Use drag and drop to fill in tags, or type tag names directly at the block terminals.
Notes: 19

## Slide 20
1
Add boolean tag “PumpRun” to the static area of the tag table.
Fill in ladder logic and tags as shown in network 4
Note: Use drag and drop to fill in tags, or type tag names directly at the block terminals.
2
Notes: 20

## Slide 21
Drag “FDBACK” from the Safety Functions Folder and place it on Network 5 as shown.
Fill in tags as shown. (Be sure to change the FDB_Time = t#500ms)
Note: Be sure to use the Multi-Instance option for the Instance Data Block “#pumpfdback_instance” when prompted during insertion the FDBACK block. Define a boolean tag “K1K2 Output” in the static area of the local tag table. Use drag and drop to fill in tags, or type tag names directly at the block terminals.
Note: Be sure to add the Feedback Time input to the block.
1
2
Notes: 21

## Slide 22
Using the Favorites Bar, add the logic as shown on Network 6
Fill in tags as shown
Note: Use drag and drop to fill in tags, or type tag names directly at the block terminals.
Note: Safety software edit is done. Save project.
1
2
Notes: 22

## Slide 23
Double-click “Main” to open the block.
Using the Favorites Bar, add the logic as shown on Network 1 and 2
Fill in tags as shown
Note: Use drag and drop to fill in tags, or type tag names directly at the block terminals.
Note: this is non-safe logic to drive indicators.
1
2
Notes: 23

## Slide 24
1
2
3
Using the Favorites Bar, add the logic as shown on Network 3
Fill in tags as shown
Save project.
Note: Use drag and drop to fill in tags, or type tag names directly at the block terminals.
Note: this is non-safe logic to drive indicators.
Notes: 24

## Slide 25
Highlight PLC_1 in the project tree
Press the Download button in the Toolbar
When the Extended download window appears, set PG/PC interface as shown.
Press “Start search”
Highlight S7-1200 in the list (Note: some PLC was factory reset and might not have an assigned IP Address, each S7-1200 CPU may have a different device name)
Press “Load”
1
2
3
4
5
6
Notes: 25

## Slide 26
1. Continue without synchronization if you see this message.
1
Notes: 26

## Slide 27
Select “Stop all” and Press “Load”
1
Notes: 27

## Slide 28
Change Start modules to “Start Module”
Press “Finish”
1
2
Notes: 28

## Slide 29: Workshop: Commissioning and Testing
Check LED status
Press reset button
Test Estop function
Press Start/Stop button and monitor outputs
Go online with the PLC and monitor logic flows(use the “goggle”—Monitoring on/off)

## Slide 30: Workshop: Documentation and Safety Acceptance Test
Safety Summary can be printed by right-click on “Safety Administration”—”Print” in offline mode.
1

## Slide 31: Workshop: Documentation and Safety Acceptance Test
Safety Signatures and time stamps are available to verify online/offline Safety Software consistency.
1

## Slide 32: Workshop Pump and VFD Control using S7-1200F
Implement new safety function for VFD control usng RFID Door Switch, using wiring diagram on page 4(Green wiring).
To save time, retrieve project “1200F vs Safety Relays Workshop Complete FY19” from the workshop folder and download “PLC_Failsafe” program to the demo unit.
Function test
Finish the final workshop exercise based on the demo unit.
Notes: 32

## Slide 33: Thank you for attending!
Help us to better serve you! Please take a moment for our survey.
Add Survey Monkey Link and QR code to follow

## Slide 34: Thank you for attending!
Help us to better serve you! Please take a moment for our survey.